| Fuel Dispensing Facilities Checklist Suggested frequency Quarterly |
| --- |
| Municipality | Inspection Date: 201___ |
| Name of Inspector: | Title: |
| Location Surveyed: |
| Guidelines for Fuel Dispensing Islands per NFPA 30 A & N.J.S.A. 34:3A-4 |
| # | Need work | OK | N/A | Write line # & comments on back for each needs work item |
|  |  |  |  | Dispensing pumps located at least 10‘from property lines? |
|  |  |  |  | Pumps located at least 10 feet from combustible structures? |
|  |  |  |  | For above ground tanks; debris and vegetation cut back 10’? |
|  |  |  |  | Do natural grade / curbs prevent drainage toward any structures? |
|  |  |  |  | Are the pumps locked when not in service? |
|  |  |  |  | Dispensing pumps at least 20‘from fixed sources of ignition? |
|  |  |  |  | Is all electrical wiring in rigid continuous (unbroken) conduit? |
|  |  |  |  | Emergency shut off switch located more than 20’ but within 100’? |
|  |  |  |  | Does activation of the E-Switch sound an alarm? |
|  |  |  |  | Do you document a MONTHLY test of the Audible alarm? (New in ‘18) |
|  |  |  |  | Does activation of the E-Switch notify Fire Dept? |
|  |  |  |  | Is there another means of summoning emergency aid? Phone? |
|  |  |  |  | Is there a minimum 2A: 40 B: C fire extinguisher available? 34.3A |
|  |  |  |  | Extinguisher mounted no more than 75‘from the pump? |
|  |  |  |  | E-switch clearly identified with a sign? |
|  |  |  |  | Is an emergency instructions sign posted? |
|  |  |  |  | Is there a “Stop engine - No Smoking” sign? 34.3A |
|  |  |  |  | Above ground tanks have CAS #? Gas: 86290-81-5 Diesel: 68476-34-6 |
|  |  |  |  | “Warning” signs against unapproved containers? |
|  |  |  |  | Is there a warning sign requiring filling cans on ground? |
|  |  |  |  | Each type of dispensing pump labeled as to product? |
|  |  |  |  | Are the NFPA diamonds posted & visible to FD? |
|  |  |  |  | Hose nozzles marked as meeting the standards of UL 842 |
|  |  |  |  | Auto dispensing limited to 25 gallons? |
|  |  |  |  | Hoses equipped with self closing nozzles? |
|  |  |  |  | Retractors: Must work properly (New in ‘18) |
|  |  |  |  | Hoses equipped with Auto-latch clips? |
|  |  |  |  | Emergency breakaway device installed on hose at each pump? |
|  |  |  |  | Hoses are free of defects, damage or cuts? |
|  |  |  |  | Is the apron for vehicles constructed of concrete? Any spill berm? |
|  |  |  |  | Pumps protected against collision by islands or bollards. |
|  |  |  |  | Are the sumps clean and empty? Keep monthly records? (New in ‘18) |
|  |  |  |  | Is the island pad at least 6” high and constructed of concrete? |
|  |  |  |  | Above ground tanks are double walled? |
|  |  |  |  | In lieu of above; do tanks have secondary containment? |
|  |  |  |  | Are the emergency environmental relief valves inspected ¼ ly? |
|  |  |  |  | Is there a spill kit in the area? (check EJIF for NJ DEP guidance) |
|  |  |  |  | Is there a fire detection __ or suppression system? __ |
|  |  |  |  | If yes, are systems inspected annually by a 3rd party vendor? |